(ACE Paper 40/2001)

for advice

Water Pollution Control Ordinance, Chapter 358

Proposed Amendments to the Technical Memorandum on Effluent Standards

Purpose

This paper seeks Members’ advice on the proposed amendments to the Technical Memorandum on Effluent Standards (TM) promulgated under section 21 of the Water Pollution Control Ordinance, Cap 358 (WPCO).

Background

2.	Under the WPCO, effluent discharges into the drainage systems or environmental waters of Hong Kong are regulated by means of a licensing system administered by the Director of Environmental Protection (the Authority).  A TM issued under the WPCO sets out the limits of the physical characteristics and chemical components of effluents that are acceptable for discharge to different receiving systems, namely foul sewers, inland and coastal waters.  In issuing or renewing a discharge licence, the Authority makes reference to the TM for the purpose of fixing the licence conditions.

3.	The Secretary for the Environment and Food is empowered under the WPCO to issue a TM, which must first be published in the Gazette and then laid on the table of the Legislative Council (LegCo) for “negative vetting” before it can be formally adopted. Under the “negative vetting” procedure, the Council has in general a period of 28 days within which to propose amendments.  Any amendments have to be proposed by a Resolution of the Council.  If no such Resolution is passed before the expiry of the negative vetting period, the new or amended TM then comes into operation.  The existing TM was issued by the then Secretary for Planning, Environment and Lands in 1991.  It sets out the effluent standards in 12 tables for discharges to different receiving systems.  Each table has up to 34 determinants and up to 13 discharge flow bands.  Contaminant limits vary with the rate of effluent being discharged.

The Review

4.	Since the promulgation of the current TM, the WPCO has been extended to cover the whole territory. At the same time, Hong Kong’s economic structure has changed and wastewater treatment has been enhanced.  Taking into account these factors, we initiated a review of the TM in 1998 with the aim of simplifying it, and ensuring that the effluent standards specified were relevant to current conditions and environmental requirements.

5.	In conducting the review, we had taken into account various factors including the existing groupings of the different receiving systems, the requirements of those systems from the point of view of protection of the environment, the nature and volume of existing discharges, and currently available wastewater treatment techniques.  The review was completed in March 2000.  Proposals for a new structure and new standards were then drawn up and distributed to 35 different external stakeholder groups, including green groups, academics and relevant trade associations for consultation.  A list of those who participated in the process is at Annex I.   An introductory briefing was held in October 2000 to explain the background to the review and go over in detail the technical approach adopted.  Five further meetings were convened to discuss specific aspects of the proposals.

6.	The original proposals were generally well received by consultees except in three main areas as follows –

(a)	The proposal to set the standards for any flow above 1,000 m3/day on a case-by-case basis.  Several of the main trade groups consulted (e.g. the electroplating, bleaching & dyeing and petroleum trades, and Hong Kong General Chamber of Commerce) initially expressed reservations about this proposal. Their concern was that they might be faced with onerous new requirements upon licence renewal, without time to adjust. However after further explanation, all these trade groups, with the exception of the bleaching and dyeing (B&D) trade, have accepted our commitment that for existing discharges the standard for the first renewed licence after the new TM comes into operation would in general not be more stringent than the current one. The B&D trade, on the other hand, requested that the standards should be prescribed at least for flows up to 2,000 m3/day.  After reviewing the case, we consider it more appropriate to retain our original proposal.  Further details are given in paragraphs 10 to 14 below.

(b)	The proposal to streamline flow bands which has resulted in tightening of some standards for discharges less than 10 m3/day to inshore coastal waters. The petroleum trade has expressed objection to this amendment as some petrol filling stations will be subject to more stringent standards for Total Suspended Solids (TSS), Chemical Oxygen Demand (COD) and Surfactants. After reviewing the issue, we consider it more appropriate to retain our original proposal. But taking note of the petroleum trade’s concern, we will allow the industry sufficient lead-time to upgrade any necessary treatment facilities. Further details are given in paragraphs 15 to 19 below.

(c)	The proposal for standards for oil and grease in discharges made to sewer.  The proposal was subsequently refined to take into account the feedback received.  Further details are given in paragraphs 22 to 24 below.

Proposed Amendments

7.	The following paragraphs set out the outcome of the review, the stakeholders’ comments on the outcome of the review and EPD's latest proposals on the proposed amendments to the TM taking into consideration views of stakeholders.

8.	Taking into account the latest wastewater treatment techniques, enforcement experience, international standards and the need to protect the environment, the review has resulted in the following proposals:

- to reduce the number of flow bands in each table from a maximum of 13 to two or three and set the standards for any flow above 1,000 m3/day on a case-by-case basis;

- to reduce the number of tables from 12 to 6 for discharges to different kinds of receiving systems; and

- to amend some of the requirements regarding the nature and concentration of pollutants and the discharge location.

9.	The originally proposed new standards are shown in Table A1 of Annex II.  Tables A2 – A7 of Annex II compare the proposed standards with the existing standards for easy reference. The major amendments are highlighted below.

Setting the standards for any flow above 1,000 m3/day on a case-by-case basis

10.	Under the existing TM, standards for flows above 6,000 m3/day are set on a case-by-case basis.  As a flow of 1,000 m3/day is already equivalent to the volume of wastewater discharged from 3,000 people and this scale of flow can have a relatively significant impact on the receiving system, we propose to extend this case-by-case arrangement to the flows between 1,000 m3/day and 6,000 m3/day as well to ensure better protection for the receiving systems.  According to our licensing record, about 99% of the discharges are below 1,000 m3/day, which means the majority of the discharges will still have their standards prescribed by the TM.

11.	Several of the trade groups consulted (electroplating, bleaching & dyeing, petroleum, and Hong Kong General Chamber of Commerce) expressed reservations about this proposal as they worried that the government may impose more stringent standards in the future for flows above 1,000 m3/day.  Having taken note of the concern of the trade groups, we have reviewed their discharge conditions (e.g. flow rate, discharge location, and wastewater characteristics) and concluded that the standards for their first renewed licences after the new TM comes into operation will in general not be more stringent than the standards they are now subject to, provided the principal discharge characteristics remain unchanged.  This will allow appropriate lead-time for the licensees to adjust wastewater treatment methods, if necessary.

12.	With the exception of the B&D trade, the stakeholders were satisfied with our commitment and no longer objected to this proposal.  The B&D trade, on the other hand, maintained that they needed a clear picture of the future standards and requested that the standards should be prescribed, at least up to 2,000 m3/day.

13.	Among the B&D discharges (less than 200), more than 90% are less than 1,000 m3/day and hence already subject to the prescribed standards.  However, even if the prescribed standards were to be extended to 2,000 m3/day some 3% of the B&D discharges would still be subject to the case-by-case assessment.

14.	While it is possible to add another flow band for flows between 1,000 to 2,000 m3/day or for even higher flow rates, this will defeat the purpose of the streamlining. It would also weaken our ability to provide more effective protection to downstream systems. We consider that with the commitment not to impose more stringent standards for the first renewed licence, there will be sufficient lead-time for the licensees to adjust the treatment facilities, if necessary, to meet any new standards that may be required for the larger flow bands.  Hence, we propose to maintain the original proposal.

Streamlining of flow bands

15.	At present, some tables in the TM have effluent standards for as many as 13 flow bands (three to seven flow bands for flows below 1,000 m3/day and one to six flow bands for flows between 1,000 and 6,000 m3/day). To make these tables less complicated, we propose to reduce the number of flow bands to two in general, i.e. <100 m3/day, and 100 to 1000 m3/day.  There will no longer be any flow band for flows exceeding 1,000 m3/day as we plan to set the standards for such flows on a case-by-case basis (paragraph 10 above).

16.	However, experience has shown that the majority of discharges to foul sewer are very small (over 60% are less than 10 m3/day) with many of the treatment facilities housed in multi-storey buildings.  In view of the low unit flows, there can be practical difficulties in treating wastewaters from these establishments to a very high standard. Thus, we propose three flow bands should be used for discharges to foul sewers, with generally more relaxed standards for flows below 10 m3/day.  The new flow bands for which standards will be prescribed are as follows:

| Receiving system | Flow bands |
| --- | --- |
| Foul sewer | £10, >10 to £100, >100 to £1000 m3/day |
| Inland waters | £100, >100 to £1000 m3/day |
| Coastal waters | £100, >100 to £1000 m3/day |

17.	Nevertheless, to reduce the flow bands from the existing 13 to two or three, some of standards will have to be adjusted in order to fit into the new system.

18.	As a result of the streamlining of flow bands, the TSS, COD and surfactants standards for discharges less than 10 m3/day to inshore coastal waters will have to be tightened from the existing 50/100/20 mg/L respectively to 30/80/15 mg/L. Petroleum trade has objected to this amendment as about 30 out of 200 or so petrol filling stations will be subject to the tightened standards and they argue that there is no practical and feasible way to comply with the standards.  Petroleum trade is the only stakeholder who expressed reservations about this proposal during the consultation exercise.

19.	However, we do not consider the objection well justified. The new standards are in fact the same as those that need to be met by existing petrol filling stations which discharge into inland waters.  They also follow the spirit of the TM that any discharge made to a receiving water body with smaller assimilative capacity (e.g. inshore coastal waters and inland waters) should be subject to relatively more stringent standards.  We anticipate that, with improvement in house-keeping and proper segregation of discharge streams, it is possible to meet the new standards as the wastewater quantity concerned is only 10 m3/day or less.  If upgrading of a treatment facility is found to be necessary for some petrol filling stations, we will allow ample time for the work.  Having considered the above, we propose to maintain the original proposal.

New grouping of inland waters

20.	At present, inland waters are divided into four groups.  But our review concluded that this is no longer necessary bearing in mind the existing water quality objectives for inland waters, and the general use patterns.  We propose to reduce the number of inland water groups from four to two, namely one for abstraction for potable supply (which would be those waters within gazetted Water Gathering Grounds), and one for the remainder.  This will streamline the administrative work in licensing under WPCO, give a clearer picture to the public on inland water grouping, and avoid disputes in classification of inland waters.  The existing and the proposed inland water groups are shown below:

| Existing Grouping | Proposed Grouping |
| --- | --- |
| A | Abstraction for potable water supply | I | Abstraction for potable water supply |
| B | Irrigation | II | Irrigation, pond fish culture, secondary contact recreation, general amenity and other general uses |
| C | Pond fish culture |  |  |
| D | General amenity and secondary contact recreation |  |  |

New grouping of coastal waters

21.	Taking into account the hydrodynamic condition and assimilative capacity of different water bodies, we propose to reduce the existing coastal water groups from six to three.  The existing and proposed coastal water groups are shown below:

| Existing Grouping | New Grouping |
| --- | --- |
| I. | Coastal waters of Tolo Harbour and Port Shelter Water Control Zones (WCZs) | A. | Semi-enclosed water bodies. These include Tolo Harbour, Port Shelter, Deep Bay, Tai Tam Bay and Junk Bay. (Their locations are shown in the Figure enclosed.) |
| II. | Coastal waters of Deep Bay WCZ |  |  |
| IIIa. | Inshore waters of Victoria Harbour WCZ | B. | Inshore waters of all WCZs except those falling within semi-enclosed water bodies (i.e. Group A above) |
| IIIb. | Inshore waters of other WCZs |  |  |
| IVa. | Marine waters of Victoria Harbour WCZ | C. | Marine waters of all WCZs except those falling within semi-enclosed water bodies (i.e. Group A above) |
| IVb. | Marine waters of other WCZs |  |  |

Revision of oil and grease (O&G) standards for discharge to sewer

22.	At present, the TM specifies O&G standards ranging from 20 mg/L to 100 mg/L for discharge to foul sewer.  The higher the flow rate, the more stringent the standards will be.  Having considered the conditions of the local catering industry and the standards applied in other places with cooking styles similar to Hong Kong (such as Singapore, Malaysia and the Mainland), we initially proposed to set the O&G standard at 100 mg/L across the board for flows up to 1,000 m3/day. –

23.	During the consultation meetings, the catering trade asked for further relaxation of the proposed standard for those restaurants that discharge less than 100 m3/day as follows:

| Flow | O&G standard |
| --- | --- |
|  | Original proposal put forward for public consultation | Trade’s proposal |
| £ 10 m3/day | 100 mg/L | 200 mg/L |
| > 10 m3/day, but £ 100 m3/day | 100 mg/L | 150 mg/L |
| >100 m3/day, but £1000 m3/day | 100 mg/L | 100 mg/L |

24.	Academics and wastewater treatment professionals attending the consultation meetings generally supported the standards proposed by the catering trade and considered that such a relaxation would not undermine the primary purpose of setting the O&G standard, i.e. to protect the downstream sewerage network and treatment facilities.  We therefore propose to adopt the standards as suggested by the trade.

Repeal of the prohibition of petroleum hydrocarbon for discharges to sewer

25.	The existing TM prohibits any discharge of petroleum hydrocarbon to foul sewers or directly to the environment.  Upon review of practices elsewhere such as Australia, the USA, Germany and the Mainland, we find this restriction overly stringent for discharges to sewer.  Thus, we propose to repeal the prohibition for discharge to sewer and set a standard at 100 mg/L.  The standard is in line with overseas standards (e.g. the USA and Germany).  Given the relatively low flows of petroleum-contaminated wastewater (which account for less than 1% of the wastewater discharged to sewers), we consider the proposed standard adequate for the protection of downstream treatment facilities and receiving waters.  Nonetheless, owing to the relatively small assimilative capacity of the inland and coastal waters in relation to the nature of the substance, direct discharge of the substance to these water bodies will remain prohibited in the new TM.

Revision of effluent standards for toxic metals and toxic substances

26.	Since zinc is commonly considered as a toxic metal, we propose to include it in the toxic metal list of the new TM.  With the addition of zinc, the number of toxic metals covered in the TM will increase from 13 to 14.

27.	As a result of the significant change in the economic and industrial structure of Hong Kong, we have reviewed the effluent standards for toxic metals and toxic substances such as cyanide and phenols, which originate mainly from the industrial sector.  In doing so, we have adopted the general international approach of considering the standards needed to protect downstream treatment facilities and receiving water bodies, the possible dilution effect due to mixing with domestic sewage in the collection system, the level of treatment received before discharge and the initial dilution that can be achieved in the environment.  As a result we have concluded that there is some scope for relaxation of the standards for toxic metals and toxic substances  discharged to sewer, but a need to tighten some of the standards for direct discharges to inland and coastal waters.  The proposed new standards are shown in Table A1 of Annex II.

Tightening of nutrient standards for direct discharges to semi-enclosed waters and discharges to inland waters leading to semi-enclosed waters

28.	To protect semi-enclosed water bodies which are more susceptible to eutrophication (e.g. Tolo Harbour), stringent nutrient standards are set in the existing TM.  The re-grouping of coastal waters will lead to more coastal waters such as Junk Bay and parts of Mirs Bay and Southern Waters, including Discovery Bay and Tai Tam Bay, being classified as semi-enclosed waters. The nutrient standards for direct discharges to these areas have to be revised accordingly.

29.	Apart from control on direct discharges, we also propose that discharges to inland waters leading to these semi-enclosed waters should be subject to the same nutrient standards.  The proposal covers most of the inland waters, including those within the Deep Bay, Tolo Harbour, Port Shelter and Mirs Bay catchments.  This means a substantial tightening of nutrient standards for discharges to these inland waters. In general, the permissible limits for total nitrogen and total phosphorus are reduced up to 80% and 50% respectively.

Tightening of bacterial standard for discharges to inland waters leading to gazetted beaches and existing discharges entering a gazetted beach directly

30.	To enhance the protection of beach water quality, we propose to tighten the E. coli standard from the existing 1,000 cfu/100 mL to 100 cfu/100 mL for discharges to inland waters leading to within 100 m of the boundary of a gazetted beach, and direct discharges to coastal waters within 100 m of the boundary of a gazetted beach.  The current ban on new discharges within 100 m of the boundary of a gazetted beach will be maintained in the new TM.

New standard for total residual chlorine (TRC) for discharges to inland waters

31.	Chlorine is commonly used for disinfection of sewage.  It is however toxic to aquatic life.  Whilst a TRC standard of 1 mg/L is set down in the existing TM for discharges to coastal waters, no standard has been specified for discharges to inland waters.  To ensure protection of inland waters which generally have a smaller assimilative capacity than coastal waters, we propose to add a TRC standard of 0.2 mg/L for discharges to inland waters.

New ammonia standard for discharge to coastal waters

32.	Ammonia, particularly in unionized form, is toxic to aquatic life.  At present, ammonia standards (from  0.5 to  20 mg/L) are specified in the TM for discharges to inland waters but not for discharges to coastal waters.  We propose a new set of ammonia standards ranging from 5 to 20 mg/L for discharges to various groups of coastal waters.

Revisions of standards for conventional parameters

33.	To match the streamlined flow bands, we propose to amend slightly the standards for some conventional parameters such as BOD5, COD, and TSS.  To align our standards with current practices elsewhere, we also propose to drop the standards for some parameters such as settleable solids and conductivity.

Other revision – removal of radioactive substances from the prohibition list

34.	In the existing TM, radioactive substances are listed as prohibited substances for discharges to sewer or environmental waters.  As the current Radiation Ordinance and its subsidiary legislation already provide for comprehensive control of radioactive substances, including the proper disposal of radioactive wastes, we propose to remove radioactive substances from the TM prohibition list to avoid confusion.

Technical and environmental implications of the new TM standards

35.	The new TM standards for discharges to sewer remain largely at the existing level (for conventional parameters such as BOD5, COD, TSS, sulphide) or slightly relaxed (for metals).  As 90% of the discharges are made to sewer, most dischargers are unlikely to encounter technical difficulties in meeting the new standards.

36.	Since mid-1993, the amount of metals discharged into Victoria Harbour has dropped from over 7,000 kg/day to about 600 kg/day due to enforcement action under the WPCO and control of chemical wastes under the Waste Disposal Ordinance.  With the commissioning of Stage 1 of the Harbour Area Treatment Scheme around early 2002, metal loadings in the discharged effluent will drop further.  Thus, the slight relaxation of the standards for discharges of metals to sewer is not expected to have an impact on water quality.

37.	For environmental waters, while the standards for conventional parameters are largely kept at the existing level, the new TM will offer better environmental protection in the long term because of the tightening of E. coli, nutrient and toxic metal standards, and the introduction of the new TRC and ammonia standards.

38.	Although some dischargers may need to upgrade their treatment facilities to meet standards such as the tightened nutrient standard, such standards are achievable, with currently available technologies and professional services in the market

Public consultation

39.	We have consulted a wide range of individuals and groups who might have an interest in these proposals.  Six consultation meetings were held between October and December 2000, involving 35 groups of external stakeholders (Annex I) covering a wide spectrum of the community.  The consultees considered the amendment proposals acceptable in general but the catering trade had suggested further relaxation of the O&G standard for discharge to sewer.   In light of the consultees’ views, we propose to adopt the standards as set out in Annex II, subject to the amendments to the standards for oil and grease discharged to sewer as proposed by the trade and described in paragraph 23, and the removal of radioactive substances from the TM prohibition list as described in paragraph 34.

Legislative timetable and commencement

40.	We plan to submit the proposals for amendments to the TM to the LegCo Environmental Affairs Panel for consideration in November 2001, and table the revised TM at LegCo for negative vetting in December 2001.  Subject to amendments by LegCo, the new TM is expected to come into operation by around early 2002.

Advice to be sought

41.	Members are requested to provide their advice on the above proposed amendments to the TM.

### Environmental Protection Department

October 2001

Annex I

Water Pollution Control Ordinance, Cap.358

Review on the Technical Memorandum on Effluent Standards (TM)

# List of External Stakeholder Groups Consulted

Industrial / Commercial Associations

1. Hong Kong General Chamber of Commerce

2. Federation of Hong Kong Industries

3. Chinese Manufacturer's Association of Hong Kong

4. Textile Council of Hong Kong Limited

5. The Hong Kong Association of Textile Bleachers, Dyers, Printers and Finishers Ltd.

6. Hong Kong Electronic Industrial Association

7. Hong Kong Metal Finishing Society

8. Oil Industry Representative Committee

9. Hong Kong Association of Property Management Companies Ltd.

10. Federation of Hong Kong Hotel Owners Ltd.

11. Hong Kong Hotels Association

12. Federation of Hong Kong Restaurant Owners Ltd.

13. Hong Kong Federation of Restaurants and Related Trades (HK Fort)

14. Association of Restaurant Managers Ltd.

15. Lan Kwai Fong Association

16. The Soho Association

17. Association for Hong Kong Catering Service Management

18. The H.K. Restaurant & Eating-House M.G. Association

19. Hong Kong Catering Industry Association

Green Groups

20. The Conservancy Association

21. Friends of the Earth

22. Green Power

23. Green Lantau Association

24. Green Peace

25. The Hong Kong Marine Conservation Society

26. World Wide Fund for Nature Hong Kong

Local Academics / Tertiary Institutions

27. The University of Hong Kong

28. The Hong Kong Polytechnic University

29. The Chinese University of Hong Kong

30. City University of Hong Kong

31. The Hong Kong University of Science and Technology

32. Hong Kong Baptist University

33. The Open University of Hong Kong

Wastewater Treatment Professionals

34. Business Environment Council

35. Hong Kong Productivity Council

## Annex II

Proposed new TM standards for effluent discharged

into different receiving water bodies

(Existing standards that are different from the proposed new standards

are shaded for ease of reference)

| Table A1 | Proposed TM standards for effluent discharged into different receiving water bodies |
| --- | --- |
|  | (All units in mg/L unless otherwise stated, all figures are upper limits unless otherwise indicated) |

|  | Proposed New TM Standards |
| --- | --- |
|  | Foul Sewer | Group I Inland Waters | Group II Inland Waters | Group A Coastal Waters | Group B Coastal Waters | Group C Coastal Waters |

| Flow (m3/day) Determinand | <10 | >10 and <100 | >100 and <1000 | <100 | >100 and <1000 | <100 | >100 and <1000 | <100 | >100 and <1000 | <100 | >100 and <1000 | <100 | >100 and <1000 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

| pH (pH units) | 6-10 | 6-10 | 6-10 | 6-9 | 6-9 | 6-9 | 6-9 | 6-9 | 6-9 | 6-9 | 6-9 | 6-10 | 6-10 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Temperature (oC) | 43 | 43 | 43 | 30 | 30 | 30 | 30 | 40 | 40 | 40 | 40 | 45 | 45 |
| Color (Lovibond units) (25mm cell length) | --(1) | -- | -- | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Dissolved Oxygen | -- | -- | -- | > 4 | > 4 | -- | -- | -- | -- | -- | -- | -- | -- |
| BOD5 | 1200 | 1000 | 800 | 10 | 5 | 20 | 20 | 20 | 20 | 20 | 20 | 500 | 300 |
| COD | 3000 | 2500 | 2000 | 50 | 20 | 80 | 80 | 80 | 80 | 80 | 80 | 1000 | 600 |
| Total suspended solids | 1200 | 1000 | 800 | 10 | 5 | 30 | 30 | 30 | 30 | 30 | 30 | 500 | 300 |
| Oil & Grease | 100 | 100 | 100 | 1 | 1 | 10 | 10 | 20 | 20 | 20 | 20 | 50 | 20 |
| Surfactants | 200 | 150 | 50 | Prohibit | Prohibit | 5 | 5 | 15 | 15 | 15 | 15 | 30 | 15 |
| Hydrogen sulphide | -- | -- | -- | 0.05 | 0.05 | -- | -- | -- | -- | -- | -- | -- | -- |
| Total sulphide | 10 | 10 | 5 | 0.2 | 0.1 | 0.2 | 0.2 | 5 | 5 | 5 | 5 | 5 | 5 |
| Fluoride | -- | -- | -- | 1 | 1 | -- | -- | -- | -- | -- | -- | -- | -- |
| Sulphate | -- | -- | -- | 600 | 400 | 800 | 600 | -- | -- | -- | -- | -- | -- |
| Chloride | -- | -- | -- | 500 | 200 | 1000 | 800 | -- | -- | -- | -- | -- | -- |
| Nitrogen (Ammonia) | -- | -- | -- | 1 | 1 | 10 | 5 | 10 | 5 | 10 | 5 | 20 | 20 |
| Total nitrogen | 200 | 200 | 200 | 15 | 10 | 50 | 30 | 20 | 15 | 100 | 80 | 100 | 80 |
| Total phosphorous | 50 | 50 | 50 | 1 | 1 | 10 | 8 | 8 | 5 | 10 | 8 | 10 | 8 |
| E.coli (cfu/100ml) | -- | -- | -- | < 1 | < 1 | 1000/ 100(2) | 1000/ 100(2) | 1000/ 100(3) | 1000/ 100(3) | 1000/ 100(3) | 1000/ 100(3) | 4000 | 4000 |
| Total residual chlorine | -- | -- | -- | 0.2 | 0.2 | 0.2 | 0.2 | 1 | 1 | 1 | 1 | 1 | 1 |
| Phenols | 1 | 1 | 1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.2 |
| Cyanide | 2 | 2 | 2 | 0.05 | 0.05 | 0.05 | 0.05 | 0.1 | 0.05 | 0.10 | 0.05 | 0.5 | 0.2 |
| Boron | -- | -- | -- | 2 | 0.5 | -- | -- | -- | -- | -- | -- | -- | -- |
| Barium | -- | -- | -- | 2 | 0.5 | -- | -- | -- | -- | -- | -- | -- | -- |
| Iron | -- | -- | -- | 2 | 0.5 | 10 | 5 | 10 | 5 | 15 | 5 | 15 | 5 |
| Manganese | -- | -- | -- | 0.5 | 0.5 | -- | -- | -- | -- | -- | -- | -- | -- |
| Arsenic | 3 | 2 | 2 | 0.05 | 0.05 | -- | -- | -- | -- | -- | -- | -- | -- |
| Cadmium | 0.5 | 0.5 | 0.5 | 0.001 | 0.001 | 0.02 | 0.01 | 0.02 | 0.01 | 0.02 | 0.01 | 0.10 | 0.05 |
| Chromium | 3 | 2 | 2 | 0.05 | 0.05 | 0.2 | 0.1 | 1.0 | 0.5 | 1.0 | 0.5 | 2.0 | 1.0 |
| Copper | 5 (2)(4) | 4 (1.5)(4) | 4 (1.5)(4) | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.5 | 0.2 |
| Lead | 2 | 1 | 1 | 0.1 | 0.1 | 0.2 | 0.1 | 0.05 | 0.05 | 0.05 | 0.05 | 0.10 | 0.05 |
| Mercury | 0.2 | 0.1 | 0.1 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Nickel | 4 | 3 | 3 | -- | -- | 0.5 | 0.2 | 0.1 | 0.1 | 0.1 | 0.1 | 0.5 | 0.2 |
| Selenium | 3 | 2 | 2 | 0.01 | 0.01 | -- | -- | -- | -- | -- | -- | -- | -- |
| Sliver | 4 | 3 | 3 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |
| Zinc | 5 | 4 | 4 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Other toxic metals individually | -- | -- | -- | 0.1 | 0.1 | -- | -- | -- | -- | -- | -- | -- | -- |
| Total toxic metals | 10 | 10 | 8 | 1 | 1 | 2 | 1 | 2 | 1 | 2 | 1 | 3 | 1 |
| Hydrocarbon | 100 | 100 | 100 | -- | -- | -- | -- | -- | -- | -- | -- | -- | -- |

Note:

- "- -" means no standard is proposed for this parameter.

- 100 cfu/100mL E.coli standard is applicable for discharges to inland waters leading to 100m of the boundaries of a gazetted beach in any direction.

- 100 cfu/100mL E.coli standard is applicable for discharges within 100m of the boundaries of a gazetted beach in any direction.

- Standard in parenthesis is applicable for discharges into foul sewer leading to Government sewage treatment plants with microbial treatment.

Table A2 Standards for effluents discharged into foul sewers leading into Government sewage treatment plants

(All units in mg/L unless otherwise stated; all figures are upper limits unless otherwise indicated)

(Existing standards that are different from the proposed new standards are shaded for ease of reference)

|  | Proposed TM sewer standards | Existing TM sewer standards |
| --- | --- | --- |
| Flow rate |  | >10 | > 100 |  | >10 | >100 | >200 | >400 | >600 | >800 | >1000 | >1500 | >2000 | >3000 | >4000 | >5000 |
| (m3/day) | <10 | and | and | <10 | and | and | and | and | and | and | and | and | and | and | and | and |
| Determinand |  | <100 | <1000 |  | <100 | <200 | <400 | <600 | <800 | <1000 | <1500 | <2000 | <3000 | <4000 | <5000 | <6000 |
| pH (pH units) | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 | 6-10 |
| Temperature (0C) | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 | 43 |
| Total suspended solids | 1200 | 1000 | 800 | 1200 | 1000 | 900 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 |
| Settleable solids | --(1) | -- | -- | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 | 100 |
| BOD5 | 1200 | 1000 | 800 | 1200 | 1000 | 900 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 | 800 |
| COD | 3000 | 2500 | 2000 | 3000 | 2500 | 2200 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 | 2000 |
| Oil & Grease | 100 | 100 | 100 | 100 | 100 | 50 | 50 | 50 | 40 | 30 | 20 | 20 | 20 | 20 | 20 | 20 |
| Total sulphide | 10 | 10 | 5 | 10 | 10 | 10 | 10 | 5 | 5 | 4 | 2 | 2 | 2 | 1 | 1 | 1 |
| Sulphate | -- | -- | -- | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 1000 | 900 | 800 | 600 | 600 | 600 | 600 |
| Total nitrogen | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 200 | 100 | 100 | 100 | 100 | 100 | 100 |
| Total phosphorus | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 25 | 25 | 25 | 25 | 25 | 25 |
| Surfactants | 200 | 150 | 50 | 200 | 150 | 50 | 40 | 30 | 25 | 25 | 25 | 25 | 25 | 25 | 25 | 25 |
| Iron | -- | -- | -- | 30 | 25 | 25 | 25 | 15 | 12.5 | 10 | 7.5 | 5 | 3.5 | 2.5 | 2 | 1.5 |
| Boron | -- | -- | -- | 8 | 7 | 6 | 5 | 4 | 3 | 2.4 | 1.6 | 1.2 | 0.8 | 0.6 | 0.5 | 0.4 |
| Barium | -- | -- | -- | 8 | 7 | 6 | 5 | 4 | 3 | 2.4 | 1.6 | 1.2 | 0.8 | 0.6 | 0.5 | 0.4 |
| Mercury | 0.2 | 0.1 | 0.1 | 0.2 | 0.15 | 0.1 | 0.1 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Cadmium | 0.5 | 0.5 | 0.5 | 0.2 | 0.15 | 0.1 | 0.1 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Copper | 5 | 4 | 4 | 4 | 4 | 4 | 3 | 1.5 | 1.5 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
|  | (2.0)(2) | (1.5) | (1.5) | (1.5) | (1) | (1) | (1) | (0.8) | (0.6) | (0.5) | (0.4) | (0.3) | (0.2) | (0.15) | (0.1) | (0.05) |
| Nickel | 4 | 3 | 3 | 4 | 3 | 3 | 2 | 1.5 | 1 | 1 | 0.8 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 |
| Chromium | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0.7 | 0.6 | 0.4 | 0.3 | 0.2 | 0.1 | 0.1 | 0.1 |
| Zinc | 5 | 4 | 4 | 5 | 5 | 4 | 3 | 1.5 | 1.5 | 1 | 0.8 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 |
| Silver | 4 | 3 | 3 | 4 | 3 | 3 | 2 | 1.5 | 1.5 | 1 | 0.8 | 0.7 | 0.7 | 0.6 | 0.6 | 0.6 |
| Arsenic | 3 | 2 | 2 | 2.5 | 2.2 | 2 | 1.5 | 1 | 0.7 | 0.6 | 0.4 | 0.3 | 0.2 | 0.15 | 0.12 | 0.1 |
| Lead | 2 | 1 | 1 | 2.5 | 2.2 | 2 | 1.5 | 1 | 0.7 | 0.6 | 0.4 | 0.3 | 0.2 | 0.15 | 0.12 | 0.1 |
| Selenium | 3 | 2 | 2 | 2.5 | 2.2 | 2 | 1.5 | 1 | 0.7 | 0.6 | 0.4 | 0.3 | 0.2 | 0.15 | 0.12 | 0.1 |
| Total toxic metals | 10(3) | 10(3) | 8(3) | 10(4) | 10(4) | 8(4) | 7(4) | 3(4) | 2(4) | 2(4) | 1.6(4) | 1.4(4) | 1.2(4) | 1.2(4) | 1.2(4) | 1(4) |
| Cyanide | 2 | 2 | 2 | 2 | 2 | 2 | 1 | 0.7 | 0.5 | 0.4 | 0.27 | 0.2 | 0.13 | 0.1 | 0.08 | 0.06 |
| Phenols | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.7 | 0.5 | 0.4 | 0.27 | 0.2 | 0.13 | 0.1 | 0.1 | 0.1 |
| Hydrocarbon | 100 | 100 | 100 | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit |

Note:

(1)	“--” means no standard is proposed for this parameter.

(2)	Standard in parenthesis is applicable for discharges to foul sewer leading to Government sewage treatment plants with microbial treatment.

(3)	The new “Total Toxic Metals” limit applies to sum of antimony, arsenic, beryllium, cadmium, chromium, copper, lead, mercury, nickel, selenium, silver, thallium, vanadium and zinc.

(4)	The existing “Total Toxic Metals” limit applies to sum of antimony, arsenic, beryllium, cadmium, chromium, copper, lead, mercury, nickel, selenium, silver, thallium and vanadium.

| Table A3 | Standards for effluents discharged into Group I inland waters. |
| --- | --- |
|  | (All units in mg/L unless otherwise stated; all figures are upper limits unless otherwise indicated) |

|  | Proposed New TM Standards | Existing TM Standards |
| --- | --- | --- |
| Flow rate (m3/day) Determinand | <100 | >100 and <1000 | <10 | >10 and <100 | >100 and <500 | >500 and <1000 | >1000 and <2000 |
| pH (pH units) | 6-9 | 6-9 | 6.5-8.5 | 6.5-8.5 | 6.5-8.5 | 6.5-8.5 | 6.5-8.5 |
| Temperature (oC) | 30 | 30 | 35 | 35 | 30 | 30 | 30 |
| Color (Lovibond units) (25mm cell length) | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Conductivity (s/cm at 20oC) | --(1) | -- | 1000 | 1000 | 1000 | 1000 | 1000 |
| Dissolved Oxygen | >4 | >4 | >4 | >4 | >4 | >4 | >4 |
| BOD5 | 10 | 5 | 10 | 10 | 5 | 5 | 5 |
| COD | 50 | 20 | 50 | 50 | 20 | 20 | 10 |
| Total suspended solids | 10 | 5 | 10 | 10 | 5 | 5 | 5 |
| Oil & Grease | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Surfactants | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit | Prohibit |
| Hydrogen sulphide | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 |
| Total sulphide | 0.2 | 0.1 | 0.2 | 0.2 | 0.1 | 0.1 | 0.1 |
| Fluoride | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 |
| Sulphate | 600 | 400 | 800 | 600 | 500 | 400 | 200 |
| Chloride | 500 | 200 | 800 | 500 | 500 | 200 | 200 |
| Nitrogen (Ammonia) | 1 | 1 | 1 | 1 | 1 | 1 | 0.5 |
| Nitrate + Nitrite | -- | -- | 15 | 15 | 15 | 10 | 10 |
| Total nitrogen | 15 | 10 | -- | -- | -- | -- | -- |
| Total reactive phosphorus | -- | -- | 1 | 0.7 | 0.7 | 0.5 | 0.5 |
| Total phosphorus | 1 | 1 | -- | -- | -- | -- | -- |
| E.coli (cfu/100ml) | <1 | <1 | <1 | <1 | <1 | <1 | <1 |
| Total residual chlorine | 0.2 | 0.2 | -- | -- | -- | -- | -- |
| Phenols | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |
| Cyanide | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.02 |
| Boron | 2 | 0.5 | 2 | 2 | 1 | 0.5 | 0.5 |
| Barium | 2 | 0.5 | 2 | 2 | 1 | 0.5 | 0.5 |
| Iron | 2 | 0.5 | 2 | 2 | 1 | 0.5 | 0.5 |
| Manganese | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 | 0.5 |
| Arsenic | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 |
| Cadmium | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Chromium | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 | 0.05 |
| Copper | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.2 | 0.1 |
| Lead | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |
| Mercury | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 | 0.001 |
| Selenium | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 |
| Zinc | 1 | 1 | 1 | 1 | 1 | 1 | 1 |
| Other toxic metals individually | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 | 0.1 |
| Total toxic metals | 1 | 1 | 0.3 | 0.3 | 0.2 | 0.2 | 0.15 |

Note :

(1)	"- -"  means no standard is proposed for this parameter

| Table A4 | Standards for effluents discharged into Group II inland waters. |
| --- | --- |
|  | (All units in mg/L unless otherwise stated; all figures are upper limits unless otherwise indicated) |

|  | Proposed New TM Standards | Existing TM Standards |
| --- | --- | --- |
| Flow rate (m3/day) Determinand | <100 | >100 and <1000 | <100 | >100 and <200 | >200 and <400 | >400 and <500 | >500 and <600 | >600 and <800 | >800 and <1000 | >1000 and <1500 | >1500 and <2000 | >2000 and <3000 |
| pH (pH units) | 6-9 | 6-9 | 6-8.5(1) 6-9(2) 6-10(3) | 6-8.5 6-9 6-10 | 6-8.5 6-9 6-10 | 6-8.5 6-9 6-10 | 6-8.5 6-9 6-10 | 6-8.5 6-9 6-10 | 6-8.5 6-9 6-10 | 6-8.5 6-9 6-10 | 6-8.5 6-9 6-10 | 6-8.5 -- 6-10 |
| Temperature (oC) | 30 | 30 | 35 30 30 | 35 30 30 | 30 30 30 | 30 30 30 | 30 30 30 | 30 30 30 | 30 30 30 | 30 30 30 | 30 30 30 | 30 -- 30 |
| Color (Lovibond units) (25mm cell length) | 1 | 1 | 1 1 1 | 1 1 1 | 1 1 1 | 1 1 1 | 1 1 1 | 1 1 1 | 1 1 1 | 1 1 1 | 1 1 1 | 1 -- 1 |
| BOD5 | 20 | 20 | 20 20 20 | 20 15 20 | 20 15 20 | 20 15 20 | 20 10 20 | 20 10 20 | 20 10 20 | 20 5 20 | 20 5 20 | 20 -- 20 |
| COD | 80 | 80 | 80 80 80 | 80 60 80 | 80 60 80 | 80 60 80 | 80 40 80 | 80 40 80 | 80 40 80 | 80 20 80 | 80 20 80 | 80 -- 80 |
| Total suspended solids | 30 | 30 | 30 20 30 | 30 10 30 | 30 10 30 | 30 10 30 | 30 10 30 | 30 10 30 | 30 10 30 | 30 5 30 | 30 5 30 | 30 -- 30 |
| Oil & Grease | 10 | 10 | 10 1 10 | 10 1 10 | 10 1 10 | 10 1 10 | 10 1 10 | 10 1 10 | 10 1 10 | 10 1 10 | 10 1 10 | 10 -- 10 |
| Surfactants | 5 | 5 | 5 2 15 | 5 2 15 | 5 2 15 | 5 2 15 | 5 2 15 | 5 2 15 | 5 2 15 | 5 1 15 | 5 1 15 | 5 -- 15 |
| Total sulphide | 0.2 | 0.2 | 0.2 0.2 1 | 0.2 0.2 1 | 0.2 0.2 1 | 0.2 0.2 1 | 0.2 0.2 1 | 0.2 0.2 1 | 0.2 0.2 1 | 0.2 0.1 1 | 0.2 0.1 1 | 0.2 -- 1 |
| Fluoride | --(4) | -- | 10 10 10 | 10 7 10 | 10 7 8 | 8 7 8 | 8 5 8 | 8 5 8 | 8 5 5 | 5 4 5 | 5 4 3 | 3 -- 3 |
| Sulphate | 800 | 600 | 800 800 800 | 800 600 800 | 800 600 600 | 600 600 600 | 600 400 600 | 600 400 600 | 600 400 600 | 400 200 400 | 400 200 400 | 400 -- 400 |
| Chloride | 1000 | 800 | 1000 1000 1000 | 1000 1000 1000 | 1000 1000 800 | 800 1000 800 | 800 1000 800 | 800 1000 800 | 800 1000 600 | 600 1000 600 | 600 1000 400 | 400 -- 400 |
| Nitrogen (Ammonia) | 10 | 5 | 5 2 20 | 5 2 20 | 5 2 20 | 5 2 20 | 5 2 20 | 5 2 20 | 5 2 20 | 5 1 20 | 5 1 20 | 5 -- 10 |
| Nitrate + Nitrite | -- | -- | 30 30 50 | 30 30 50 | 30 30 50 | 30 30 50 | 30 20 50 | 20 20 30 | 20 20 30 | 20 20 30 | 10 20 30 | 10 20 20 |
| Total nitrogen | 50 | 30 | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- |
| Total Phosphorus | 10 | 8 | 10 10 10 | 10 10 10 | 10 10 10 | 10 10 10 | 10 8 10 | 8 8 8 | 8 8 8 | 8 8 8 | 5 8 5 | 5 -- 5 |
| E.coli (cfu/100ml) | 1000/ 100(5) | 1000/ 100(5) | 100 1000 1000 | 100 1000 1000 | 100 1000 1000 | 100 1000 1000 | 100 1000 1000 | 100 1000 1000 | 100 1000 1000 | 100 1000 1000 | 100 1000 1000 | 100 -- 1000 |
| Total residual chlorine | 0.2 | 0.2 | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- |
| Phenols | 0.1 | 0.1 | 0.1 0.1 0.4 | 0.1 0.1 0.4 | 0.1 0.1 0.3 | 0.1 0.1 0.2 | 0.1 0.1 0.2 | 0.1 0.1 0.1 | 0.1 0.1 0.1 | 0.1 0.1 0.1 | 0.1 0.1 0.1 | 0.1 -- 0.1 |
| Cyanide | 0.05 | 0.05 | 0.1 0.05 0.4 | 0.1 0.05 0.4 | 0.1 0.05 0.4 | 0.1 0.05 0.3 | 0.1 0.05 0.3 | 0.08 0.05 0.3 | 0.08 0.05 0.2 | 0.05 0.01 0.1 | 0.05 0.01 0.1 | 0.03 -- 0.05 |

| Table A4 | Standards for effluents discharged into Group II inland waters. (Cont’d) |
| --- | --- |
|  | (All units in mg/L unless otherwise stated; all figures are upper limits unless otherwise indicated) |

|  | Proposed New TM Standards | Existing TM Standards |
| --- | --- | --- |
| Flow rate (m3/day) Determinand | <100 | >100 and <1000 | <100 | >100 and <200 | >200 and <400 | >400 and <500 | >500 and <600 | >600 and <800 | >800 and <1000 | >1000 and <1500 | >1500 and <2000 | >2000 and <3000 |
| Boron | -- | -- | 5 10 5 | 5 5 5 | 4 5 4 | 3 5 3.5 | 3 4 3.5 | 2.5 4 2.5 | 2 4 2 | 1.5 2 1.5 | 1 2 1 | 0.5 -- 0.7 |
| Barium | -- | -- | 5 1 5 | 5 1 5 | 4 1 4 | 3 1 3.5 | 3 1 3.5 | 2.5 1 2.5 | 2 1 2 | 1.5 0.5 1.5 | 1 0.5 1 | 0.5 -- 0.7 |
| Iron | 10 | 5 | 10 0.5 10 | 10 0.4 10 | 8 0.4 8 | 7 0.4 7 | 7 0.3 7 | 5 0.3 5 | 4 0.3 4 | 3 0.2 2.7 | 2 0.2 2 | 1 -- 1.3 |
| Cadmium | 0.02 | 0.01 | 0.001 0.001 0.1 | 0.001 0.001 0.1 | 0.001 0.001 0.05 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 -- 0.001 |
| Chromium | 0.2 | 0.1 | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- |
| Copper | 0.2 | 0.2 | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.05 -- | -- 0.05 -- | -- 0.05 -- | -- 0.05 -- | -- 0.05 -- | -- -- -- |
| Lead | 0.2 | 0.1 | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.1 -- | -- 0.1 -- | -- -- -- |
| Mercury | 0.001 | 0.001 | 0.001 0.001 0.1 | 0.001 0.001 0.1 | 0.001 0.001 0.05 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 0.001 0.001 | 0.001 -- 0.001 |
| Nickel | 0.5 | 0.2 | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.2 -- | -- 0.1 -- | -- 0.1 -- | -- -- -- |
| Selenium | -- | -- | 0.2 0.1 -- | 0.2 0.1 -- | 0.2 0.1 -- | 0.2 0.1 -- | 0.2 0.05 -- | 0.2 0.05 -- | 0.2 0.05 -- | 0.1 0.05 -- | 0.1 0.05 -- | 0.1 -- -- |
| Sliver | -- | -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- 0.1 -- | -- -- -- |
| Zinc | 1 | 1 | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- | -- -- -- |
| Other toxic metals individually | -- | -- | 0.5 0.5 1 | 0.5 0.4 1 | 0.5 0.4 1 | 0.2 0.4 0.8 | 0.2 0.3 0.8 | 0.2 0.3 0.8 | 0.2 0.3 0.5 | 0.1 0.2 0.5 | 0.1 0.2 0.2 | 0.1 -- 0.2 |
| Total toxic metals | 2 | 1 | 2 0.5 2 | 2 0.4 2 | 1.5 0.4 2 | 1 0.4 1.6 | 1 0.3 1.6 | 0.5 0.3 1.6 | 0.5 0.3 1 | 0.2 0.2 1 | 0.2 0.2 0.5 | 0.2 -- 0.4 |

Note:

(1)	Existing TM standards for discharge to Group B inland waters.

(2)	Existing TM standards for discharge to Group C inland waters.

- Existing TM standards for discharge to Group D inland waters.

- "- -"  means no standard is proposed for this parameter.

(5)	100 cfu/100mL E.coli standard is applicable for discharges t inland water leading to 100m of the boundaries of a gazetted beach.

| Table A5 | Standards for effluents discharged into Group A coastal waters |  |
| --- | --- | --- |
|  | (All units in mg/L unless otherwise stated; all figures are upper limits unless otherwise indicated) |
|  | Proposed TM Standards | Existing TM Standards |
| Flow rate (m3/day) Determinand | <100 | >100 and <1000 | <10 | >10 and <200 | >200 and <400 | >400 and <600 | >600 and <800 | >800 and <1000 | >1000 and <1500 | >1500 and <2000 | >2000 and <3000 | >3000 and <4000 | >4000 and <5000 | >5000 and <6000 |
| pH (pH units) | 6-9 | 6-9 | 6-9(1) 6-9(2) | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 |
| Temperature (oC) | 40 | 40 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 |
| Color (Lovibond units) (25mm cell length) | 1 | 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 |
| BOD5 | 20 | 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 10 10 | 10 10 | 10 10 | 10 10 | 10 10 | 10 10 |
| COD | 80 | 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 50 50 | 50 50 | 50 50 | 50 50 | 50 50 | 50 50 |
| Total suspended solids | 30 | 30 | 30 50 | 30 50 | 30 50 | 30 50 | 30 50 | 30 50 | 15 25 | 15 25 | 15 25 | 15 25 | 15 25 | 15 25 |
| Oil & Grease | 20 | 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 10 10 | 10 10 | 10 10 | 10 10 | 10 10 | 10 10 |
| Surfactants | 15 | 15 | 15 15 | 15 15 | 15 15 | 15 15 | 15 15 | 15 15 | 10 10 | 10 10 | 10 10 | 10 10 | 10 10 | 10 7 |
| Total sulphide | 5 | 5 | 5 5 | 5 5 | 5 5 | 5 5 | 5 5 | 5 5 | 2.5 2.5 | 2.5 2.5 | 1.5 1.5 | 1 1 | 1 1 | 0.5 0.5 |
| Nitrogen (Ammonia) | 10 | 5 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Total nitrogen | 20 | 15 | 20 100 | 20 100 | 20 100 | 15 100 | 15 100 | 15 100 | 15 80 | 15 80 | 10 50 | 10 50 | 10 50 | 10 50 |
| Total Phosphorus | 8 | 5 | 8 10 | 8 10 | 5 10 | 5 10 | 5 10 | 5 10 | 5 8 | 5 8 | 5 5 | 5 5 | 5 5 | 5 5 |
| E.coli (cfu/100ml) | 1000/ 100(3) | 1000/ 100(3) | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 | 1000 1000 |
| Total residual chlorine | 1 | 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 |
| Phenols | 0.1 | 0.1 | 0.5 0.5 | 0.5 0.5 | 0.5 0.4 | 0.25 0.3 | 0.25 0.25 | 0.25 0.2 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Cyanide | 0.1 | 0.05 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.08 | 0.05 0.06 | 0.05 0.04 | 0.03 0.03 | 0.02 0.02 | 0.02 0.01 | 0.01 0.01 |
| Boron | --(4) | -- | 5 5 | 4 4 | 3 3 | 2.5 2.5 | 2 2 | 1.6 1.6 | 1.1 1.1 | 0.8 0.8 | 0.5 0.5 | 0.4 0.4 | 0.3 0.3 | 0.2 0.2 |
| Barium | -- | -- | 5 5 | 4 4 | 3 3 | 2.5 2.5 | 2 2 | 1.6 1.6 | 1.1 1.1 | 0.8 0.8 | 0.5 0.5 | 0.4 0.4 | 0.3 0.3 | 0.2 0.2 |
| Iron | 10 | 5 | 10 10 | 10 10 | 10 10 | 7 7 | 5 5 | 4 4 | 2.7 3 | 2 2 | 1.3 1 | 1 1 | 0.8 1 | 0.6 1 |
| Cadmium | 0.02 | 0.01 | 0.1 0.1 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 |
| Chromium | 1.0 | 0.5 | 1 1 | 1 0.5 | 0.8 0.5 | 0.5 0.5 | 0.5 0.4 | 0.4 0.4 | 0.1 0.25 | 0.1 0.2 | 0.1 0.15 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Copper | 0.2 | 0.2 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Lead | 0.05 | 0.05 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Mercury | 0.001 | 0.001 | 0.1 0.1 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 |
| Nickel | 0.1 | 0.1 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Zinc | 1 | 1 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Other toxic metals individually | -- | -- | 1 1 | 1 0.5 | 0.8 0.5 | 0.5 0.5 | 0.5 0.4 | 0.4 0.4 | 0.1 0.25 | 0.1 0.2 | 0.1 0.15 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Total toxic metals | 2 | 1 | 2 2 | 2 1 | 1.6 1 | 1 1 | 1 0.8 | 0.8 0.8 | 0.2 0.5 | 0.2 0.4 | 0.2 0.3 | 0.2 0.2 | 0.14 0.14 | 0.1 0.1 |

Note :

- Existing TM standard for discharge to coastal waters of Tolo and Port Shelter Water Control Zone.

- Existing TM standard for discharge to coastal waters of Deep Bay Water Control Zone.

- 100cfu/100mL E.coli standard is applicable to discharges within 100m of the boundaries of a gazetted beach in any direction.

- "- -"  means no standard is proposed for this parameter.

| Table A6 | Standards for effluents discharged into Group B coastal waters |
| --- | --- |
|  | (All units in mg/L unless otherwise stated; all figures are upper limits unless otherwise indicated) |

|  | Proposed TM Standards | Existing TM Standards |
| --- | --- | --- |
| Flow rate (m3/day) Determinand | <100 | >100 and <1000 | <10 | >10 and <200 | >200 and <400 | >400 and <600 | >600 and <800 | >800 and <1000 | >1000 and <1500 | >1500 and <2000 | >2000 and <3000 | >3000 and <4000 | >4000 and <5000 | >5000 and <6000 |
| pH (pH units) | 6-9 | 6-9 | 6-9(1) 6-9(2) | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 | 6-9 6-9 |
| Temperature (oC) | 40 | 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 | 40 40 |
| Color(Lovibond units) (25mm cell length) | 1 | 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 |
| BOD5 | 20 | 20 | 50 50 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 |
| COD | 80 | 80 | 100 100 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 | 80 80 |
| Total suspended solids | 30 | 30 | 50 50 | 30 30 | 30 30 | 30 30 | 30 30 | 30 30 | 30 30 | 30 30 | 30 30 | 30 30 | 30 30 | 30 30 |
| Oil & Grease | 20 | 20 | 30 30 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 10 |
| Surfactants | 15 | 15 | 20 20 | 15 15 | 15 15 | 15 15 | 15 15 | 15 15 | 10 10 | 10 10 | 10 10 | 10 10 | 10 10 | 10 10 |
| Total sulphide | 5 | 5 | 5 5 | 5 5 | 5 5 | 5 5 | 5 5 | 5 5 | 2.5 2.5 | 2.5 2.5 | 1.5 1.5 | 1 1 | 1 1 | 0.5 0.5 |
| Nitrogen (Ammonia) | 10 | 5 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Total nitrogen | 100 | 80 | 100 100 | 100 100 | 100 80 | 100 80 | 100 80 | 100 80 | 80 50 | 80 50 | 50 50 | 50 50 | 50 50 | 50 30 |
| Total Phosphorus | 10 | 8 | 10 10 | 10 10 | 10 8 | 10 8 | 10 8 | 10 8 | 8 5 | 8 5 | 5 5 | 5 5 | 5 5 | 5 5 |
| E.coli (cfu/100ml) | 1000/ 100(3) | 1000/ 100(3) | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 | 5000 1000 |
| Total residual chlorine | 1 | 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 |
| Phenols | 0.1 | 0.1 | 0.5 0.5 | 0.5 0.5 | 0.5 0.5 | 0.3 0.3 | 0.25 0.25 | 0.2 0.2 | 0.13 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Cyanide | 0.10 | 0.05 | 0.2 0.2 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.05 0.05 | 0.05 0.05 | 0.03 0.03 | 0.02 0.02 | 0.02 0.02 | 0.01 0.01 |
| Boron | --(4) | -- | 5 5 | 4 4 | 3 3 | 2.7 2 | 2 2 | 1.6 1.5 | 1.1 1.1 | 0.8 0.8 | 0.5 0.5 | 0.4 0.4 | 0.3 0.3 | 0.2 0.2 |
| Barium | -- | -- | 5 5 | 4 4 | 3 3 | 2.7 2 | 2 2 | 1.6 1.5 | 1.1 1.1 | 0.8 0.8 | 0.5 0.5 | 0.4 0.4 | 0.3 0.3 | 0.2 0.2 |
| Iron | 15 | 5 | 15 15 | 10 10 | 10 10 | 7 7 | 5 5 | 4 4 | 2.7 3 | 2 2 | 1.3 1 | 1 1 | 0.8 0.8 | 0.6 0.6 |
| Cadmium | 0.02 | 0.01 | 0.1 0.1 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 |
| Chromium | 1.0 | 0.5 | 1 1 | 1 1 | 0.8 0.8 | 0.7 0.7 | 0.5 0.5 | 0.4 0.4 | 0.25 0.3 | 0.2 0.2 | 0.15 0.15 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Copper | 0.2 | 0.2 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Lead | 0.05 | 0.05 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Mercury | 0.001 | 0.001 | 0.1 0.1 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 |
| Nickel | 0.1 | 0.1 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | 0.25 0.3 | 0.2 0.2 | 0.15 0.15 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Zinc | 1 | 1 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Other toxic metals individually | -- | -- | 1 1 | 1 1 | 0.8 0.8 | 0.7 0.7 | 0.5 0.5 | 0.4 0.4 | 0.25 0.3 | 0.2 0.2 | 0.15 0.15 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Total toxic metals | 2 | 1 | 2 2 | 2 2 | 1.6 1.6 | 1.4 1.4 | 1 1 | 0.8 0.8 | 0.5 0.6 | 0.4 0.4 | 0.3 0.3 | 0.2 0.2 | 0.14 0.1 | 0.1 0.1 |

Note:

- Existing TM standard for discharge to inshore waters of Victoria Harbour Water Control Zone..

- Existing TM standard for discharge to inshore waters of Southern, Mirs Bay, Junk Bay, North Western, Eastern Buffer and Western Buffer Water Control Zone.

- 100cfu/100mL E.coli standard is applicable to discharges  within 100m of the boundaries of a gazetted beach in any direction.

"- -"  means no stnadard is proposed for this parameter.

| Table A7 | Standards for effluents discharged into Group C coastal waters. |
| --- | --- |
|  | (All units in mg/L unless otherwise stated; all figures are upper limits unless otherwise indicated) |

|  | Proposed TM Standards | Existing TM Standards |
| --- | --- | --- |
| Flow rate (m3/day) Determinand | <100 | >100 and <1000 | <10 | >10 and <200 | >200 and <400 | >400 and <600 | >600 and <800 | >800 and <1000 | >1000 and <1500 | >1500 and <2000 | >2000 and <3000 | >3000 and <4000 | >4000 and <5000 | >5000 and <6000 |
| pH (pH units) | 6-10 | 6-10 | 6-10(1) 6-10(2) | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 | 6-10 6-10 |
| Temperature (oC) | 45 | 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 | 45 45 |
| Color (Lovibond units) (25mm cell length) | 1 | 1 | 4 4 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 |
| BOD5 | 500 | 300 | 700 500 | 600 500 | 600 500 | 500 300 | 375 200 | 300 200 | 200 100 | 150 100 | 100 50 | 75 50 | 60 40 | 40 30 |
| COD | 1000 | 600 | 1500 1000 | 1200 1000 | 1200 1000 | 1000 700 | 700 500 | 600 400 | 400 300 | 300 200 | 200 150 | 100 100 | 100 80 | 85 80 |
| Total suspended solids | 500 | 300 | 700 500 | 600 500 | 600 500 | 500 300 | 375 200 | 300 200 | 200 100 | 150 100 | 100 50 | 75 50 | 60 40 | 40 30 |
| Oil & Grease | 50 | 20 | 50 50 | 50 50 | 50 50 | 30 30 | 25 25 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 | 20 20 |
| Surfactants | 30 | 15 | 30 30 | 20 20 | 20 20 | 20 20 | 15 15 | 15 15 | 15 15 | 15 15 | 15 15 | 15 15 | 15 15 | 15 15 |
| Total sulphide | 5 | 5 | 5 5 | 5 5 | 5 5 | 5 5 | 5 5 | 5 5 | 2.5 2.5 | 2.5 2.5 | 1.5 1.5 | 1 1 | 1 1 | 0.5 0.5 |
| Nitrogen (Ammonia) | 20 | 20 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Total nitrogen | 100 | 80 | 100 100 | 100 100 | 100 80 | 100 80 | 100 80 | 100 80 | 100 50 | 100 50 | 100 50 | 100 50 | 100 50 | 50 50 |
| Total Phosphorus | 10 | 8 | 10 10 | 10 10 | 10 8 | 10 8 | 10 8 | 10 8 | 10 5 | 10 5 | 10 5 | 10 5 | 10 5 | 5 5 |
| E.coli (cfu/100ml) | 4000 | 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 | 5000 4000 |
| Total residual chlorine | 1 | 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 | 1 1 |
| Phenols | 0.5 | 0.2 | 0.5 0.5 | 0.5 0.5 | 0.5 0.5 | 0.3 0.3 | 0.3 0.25 | 0.2 0.2 | 0.1 0.13 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 | 0.1 0.1 |
| Cyanide | 0.5 | 0.2 | 1 1 | 0.5 0.5 | 0.5 0.5 | 0.5 0.5 | 0.4 0.4 | 0.3 0.3 | 0.2 0.2 | 0.1 0.15 | 0.1 0.1 | 0.08 0.08 | 0.06 0.06 | 0.04 0.04 |
| Boron | --(3) | -- | 6 6 | 5 5 | 4 4 | 3.5 3.5 | 2.5 2.5 | 2 2 | 1.5 1.5 | 1 1 | 0.7 0.7 | 0.5 0.5 | 0.4 0.4 | 0.3 0.3 |
| Barium | -- | -- | 6 6 | 5 5 | 4 4 | 3.5 3.5 | 2.5 2.5 | 2 2 | 1.5 1.5 | 1 1 | 0.7 0.7 | 0.5 0.5 | 0.4 0.4 | 0.3 0.3 |
| Iron | 15 | 5 | 20 20 | 15 15 | 13 13 | 10 10 | 7.5 7 | 6 6 | 4 4 | 3 3 | 2 2 | 1.5 1.5 | 1.2 1.2 | 1 1 |
| Cadmium | 0.10 | 0.05 | 0.1 0.1 | 0.1 0.1 | 0.05 0.1 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 |
| Chromium | 2.0 | 1.0 | 2 2 | 1.5 1.5 | 1 1.2 | 0.8 0.8 | 0.6 0.6 | 0.5 0.5 | 0.32 0.32 | 0.24 0.24 | 0.16 0.16 | 0.12 0.12 | 0.1 0.1 | 0.1 0.1 |
| Copper | 0.5 | 0.2 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Lead | 0.10 | 0.05 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Mercury | 0.001 | 0.001 | 0.1 0.1 | 0.1 0.1 | 0.05 0.1 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 | 0.001 0.001 |
| Nickel | 0.5 | 0.2 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Zinc | 1 | 1 | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- | -- -- |
| Other toxic metals individually | -- | -- | 2 2 | 1.5 1.5 | 1 1.2 | 0.8 0.8 | 0.6 0.6 | 0.5 0.5 | 0.32 0.32 | 0.24 0.24 | 0.16 0.16 | 0.12 0.12 | 0.1 0.1 | 0.1 0.1 |
| Total toxic metals | 3 | 1 | 4 4 | 3 3 | 2 2.4 | 1.6 1.6 | 1.2 1.2 | 1 1 | 0.64 0.64 | 0.48 0.48 | 0.32 0.32 | 0.24 0.24 | 0.2 0.2 | 0.14 0.14 |

Note:

- Existing TM standard for discharge to marine waters of Victoria Harbour Water Control Zone..

- Existing TM standard for discharge to marine waters of Southern, Mirs Bay, Junk Bay, North Western, Eastern Buffer and Western Buffer Water Control Zone.

- "- -" means no standard is proposed for this parameter.

# Footnotes

If the end of the 28-day period falls on a date after the end of a LegCo session or a dissolution but on or before the day of the second sitting of the next LegCo session, the period shall be deemed to extend to and expire on the day after that second sitting of the LegCo.  LegCo may also by resolution to extend the “vetting period” to the next meeting.

The existing 13 toxic metals are antimony, arsenic, beryllium, cadmium, chromium, copper, lead, mercury, nickel, selenium, silver, thallium and vanadium.